## Note
Item Naming
Symbols NOT used in table: | . | & | - | # | ?
Do NOT change tab name | UnitCost | Cashflow
Check missing content | % | $ | Level | Group | User Guide
Cashflow
Check cashflow table matches with excel template

## UnitCost
Level 1 | Level 2 | Level 3 | Level 4 | Level 5 | Unit Price | Unit | group_1 | group_2 | group_3 | Material | Labour | Other | picture | User Guide
Substation | Transformer | 138/25kV | 25MVA | Equipment | 917461 | each | facility | substation | material | 100% | 0% | 0%
Substation | Transformer | 138/25kV | 42MVA | Equipment | 1084471 | each | facility | substation | material | 100% | 0% | 0%
Substation | Transformer | 240/138kV | 100MVA | Equipment | 2148604 | each | facility | substation | material | 100% | 0% | 0%
Substation | Transformer | 240/138kV | 200MVA | Equipment | 2361346 | each | facility | substation | material | 100% | 0% | 0%
Substation | Transformer | 240/138kV | 400MVA | Equipment | 3065949 | each | facility | substation | material | 100% | 0% | 0%
Substation | Transformer | 500/240kV | 1200MVA | Equipment | 1840250 | each | facility | substation | material | 100% | 0% | 0% |  | single phase only, 400MVA per phase
Substation | Circuit Breaker | 240kV | 1050kV | Equipment | 220201 | each | facility | substation | material | 100% | 0% | 0%
Substation | Circuit Breaker | 138kV | 650kV | Equipment | 102936 | each | facility | substation | material | 100% | 0% | 0%
Substation | Circuit Breaker | 25kV | 100kV | Equipment | 66618 | each | facility | substation | material | 100% | 0% | 0%
Substation | Current Transformer | 240kV | 2000:1 | Equipment | 29470 | each | facility | substation | material | 100% | 0% | 0%
Substation | Current Transformer | 138kV | 1200:1 | Equipment | 18599 | each | facility | substation | material | 100% | 0% | 0%
Substation | Voltage Transformer | 240kV | 1050kV | Equipment | 22916 | each | facility | substation | material | 100% | 0% | 0%
Substation | Voltage Transformer | 138kV | 650kV | Equipment | 17822 | each | facility | substation | material | 100% | 0% | 0%
Substation | Potential Transformer | 240kV | 1050kV | Equipment | 22916 | each | facility | substation | material | 100% | 0% | 0%
Substation | Potential Transformer | 138kV | 650kV | Equipment | 17822 | each | facility | substation | material | 100% | 0% | 0%
Substation | VAR Cap Bank | 240kV | xMVA | Equipment | 453511 | each | facility | substation | material | 100% | 0% | 0%
Substation | VAR Cap Bank | 138kV | xMVA | Equipment | 574078 | each | facility | substation | material | 100% | 0% | 0%
Substation | VAR Cap Bank | 25kV | xMVA | Equipment | 58455 | each | facility | substation | material | 100% | 0% | 0%
Substation | VAR Reactor | 240kV | xMVA | Equipment | 1437620 | each | facility | substation | material | 100% | 0% | 0%
Substation | VAR Reactor | 138kV | xMVA | Equipment | 1335719 | each | facility | substation | material | 100% | 0% | 0%
Substation | Station Service | SS transformer | 75kVA | Equipment | 31989 | each | facility | substation | material | 100% | 0% | 0%
Substation | Air Break | 240kV | 1050kV | Equipment | 36724 | each | facility | substation | material | 100% | 0% | 0%
Substation | Air Break | 138kV | 650kV | Equipment | 25809 | each | facility | substation | material | 100% | 0% | 0%
Substation | Air Break | 25kV | 100kV | Equipment | 21357 | each | facility | substation | material | 100% | 0% | 0%
Substation | Line Termination | 240kV | 1050kV | Equipment | 350193 | each | facility | substation | material | 100% | 0% | 0%
Substation | Line Termination | 138kV | 650kV | Equipment | 220984 | each | facility | substation | material | 100% | 0% | 0%
Substation | Main Bus | 240kV | 4000A | Equipment | 10663 | each | facility | substation | material | 100% | 0% | 0%
Substation | Main Bus | 138kV | 2000A | Equipment | 5332 | each | facility | substation | material | 100% | 0% | 0%
Substation | Control Building | 4mx14m | pre-fab | Equipment | 298575 | each | facility | substation | material | 100% | 0% | 0%
Substation | Switchgear Building | single-cell | 25kV pre-fab | Equipment | 100000 | each | facility | substation | material | 100% | 0% | 0% |  | applicable for addition or substraction cells
Substation | Protection & Control | Relays/modules/meter |  | Equipment | 33650 | each | facility | substation | material | 100% | 0% | 0%
Substation | Protection & Control | Control cables |  | Equipment | 11 | /m | facility | substation | material | 100% | 0% | 0% |  | 600m/relay or module; AWG #10 and below
Substation | Transformer | 138/25kV | 25MVA | Installation | 345507 | each | facility | substation | labour | 0% | 0% | 0%
Substation | Transformer | 138/25kV | 42MVA | Installation | 408402 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Transformer | 240/138kV | 100MVA | Installation | 809145 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Transformer | 240/138kV | 200MVA | Installation | 889262 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Transformer | 240/138kV | 400MVA | Installation | 1154609 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Transformer | 500/240kV | 1200MVA | Installation | 693022 | each | facility | substation | labour | 0% | 100% | 0% |  | single phase only, 400MVA per phase
Substation | Circuit Breaker | 240kV | 1050kV | Installation | 110605 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Circuit Breaker | 138kV | 650kV | Installation | 51704 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Circuit Breaker | 25kV | 100kV | Installation | 33462 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Current Transformer | 240kV | 2000:1 | Installation | 14803 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Current Transformer | 138kV | 1200:1 | Installation | 9342 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Voltage Transformer | 240kV | 1050kV | Installation | 11510 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Voltage Transformer | 138kV | 650kV | Installation | 8952 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Potential Transformer | 240kV | 1050kV | Installation | 11510 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Potential Transformer | 138kV | 650kV | Installation | 8952 | each | facility | substation | labour | 0% | 100% | 0%
Substation | VAR Cap Bank | 240kV | xMVA | Installation | 227795 | each | facility | substation | labour | 0% | 100% | 0%
Substation | VAR Cap Bank | 138kV | xMVA | Installation | 288354 | each | facility | substation | labour | 0% | 100% | 0%
Substation | VAR Cap Bank | 25kV | xMVA | Installation | 29361 | each | facility | substation | labour | 0% | 100% | 0%
Substation | VAR Reactor | 240kV | xMVA | Installation | 541395 | each | facility | substation | labour | 0% | 100% | 0%
Substation | VAR Reactor | 138kV | xMVA | Installation | 503020 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Station Service | SS transformer | 75kVA | Installation | 12047 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Air Break | 240kV | 1050kV | Installation | 18446 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Air Break | 138kV | 650kV | Installation | 12963 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Air Break | 25kV | 100kV | Installation | 10727 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Line Termination | 240kV | 1050kV | Installation | 175899 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Line Termination | 138kV | 650kV | Installation | 110998 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Main Bus | 240kV | 4000A | Installation | 5356 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Main Bus | 138kV | 2000A | Installation | 2678 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Control Building | 4mx14m | pre-fab | Installation | 149971 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Protection & Control | Relays/modules/meter |  | Installation | 16902 | each | facility | substation | labour | 0% | 100% | 0% | protectionRelay.JPG
Substation | Protection & Control | Control cables&trench | trenching/closing | Installation | 53 | /m | facility | substation | labour | 0% | 100% | 0%
Substation | Transformer | 138/25kV | 25MVA | Foundation | 345507 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Transformer | 138/25kV | 42MVA | Foundation | 408402 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Transformer | 240/138kV | 100MVA | Foundation | 809145 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Transformer | 240/138kV | 200MVA | Foundation | 889262 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Transformer | 240/138kV | 400MVA | Foundation | 1154609 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Transformer | 500/240kV | 1200MVA | Foundation | 693022 | each | facility | substation | labour | 0% | 100% | 0% |  | single phase only, 400MVA per phase
Substation | Circuit Breaker | 240kV | 1050kV | Foundation | 110605 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Circuit Breaker | 138kV | 650kV | Foundation | 51704 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Circuit Breaker | 25kV | 100kV | Foundation | 33462 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Current Transformer | 240kV | 2000:1 | Foundation | 14803 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Current Transformer | 138kV | 1200:1 | Foundation | 9342 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Voltage Transformer | 240kV | 1050kV | Foundation | 11510 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Voltage Transformer | 138kV | 650kV | Foundation | 8952 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Potential Transformer | 240kV | 1050kV | Foundation | 11510 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Potential Transformer | 138kV | 650kV | Foundation | 8952 | each | facility | substation | labour | 0% | 100% | 0%
Substation | VAR Cap Bank | 240kV | xMVA | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0%
Substation | VAR Cap Bank | 138kV | xMVA | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0%
Substation | VAR Cap Bank | 25kV | xMVA | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0%
Substation | VAR Reactor | 240kV | xMVA | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0%
Substation | VAR Reactor | 138kV | xMVA | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0%
Substation | Station Service | SS transformer | 75kVA | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0%
Substation | Air Break | 240kV | 1050kV | Foundation | 18446 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Air Break | 138kV | 650kV | Foundation | 12963 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Air Break | 25kV | 100kV | Foundation | 10727 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Line Termination | 240kV | 1050kV | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0%
Substation | Line Termination | 138kV | 650kV | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0%
Substation | Main Bus | 240kV | 4000A | Foundation | 5356 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Main Bus | 138kV | 2000A | Foundation | 2678 | each | facility | substation | labour | 0% | 100% | 0%
Substation | Control Building | 4mx14m | pre-fab | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0%
Substation | Civil Work | Site Development |  |  | 260 | /m² | facility | substation | labour | 0% | 100% | 0% |  | station sizing guide: new 240kV sub, 150mx135m; new 138kV sub, 135mx75m; new 240kV switching sub, 100mx100m; new 138kV switching sub, 75mx75m; 240kV site expansion, 20mx20m per major eqpmt; 138kV site expansion, 15mx15m per major eqpmt incl. excavation/backfill, fence and gate
Substation | Civil Work | Access road (7m) |  |  | 1066 | /m | facility | substation | labour | 0% | 100% | 0% |  | default length for new station is 100m, or as per measurement on map, whichever is available
Line | Structure | Wood Pole | 138kV | Tangent | 3000 | each | facility | line | material | 100% | 100% | 0%
Line | Structure | Wood Pole | 138kV | Light/Med Angle | 4500 | each | facility | line | material | 100% | 100% | 0%
Line | Structure | Wood Pole | 138kV | Heavy Angle | 5500 | each | facility | line | material | 100% | 100% | 0%
Line | Structure | Wood Pole | 138kV | Dead End | 10000 | each | facility | line | material | 100% | 100% | 0%
Line | Structure | Steel Pole | 138kV | Tangent | 22000 | each | facility | line | material | 100% | 0% | 0%
Line | Structure | Steel Pole | 138kV | Light/Med Angle | 30000 | each | facility | line | material | 100% | 0% | 0%
Line | Structure | Steel Pole | 138kV | Heavy Angle | 39000 | each | facility | line | material | 100% | 0% | 0%
Line | Structure | Steel Pole | 138kV | Dead End | 47000 | each | facility | line | material | 100% | 0% | 0%
Line | Structure | Steel Pole | 240kV | Tangent | 20000 | each | facility | line | material | 100% | 0% | 0%
Line | Structure | Steel Pole | 240kV | Light/Med Angle | 50000 | each | facility | line | material | 100% | 0% | 0%
Line | Structure | Steel Pole | 240kV | Heavy Angle | 190000 | each | facility | line | material | 100% | 0% | 0%
Line | Structure | Steel Pole | 240kV | Dead End | 205000 | each | facility | line | material | 100% | 0% | 0%
Line | Structure | Lattice Tower | 240kV | Tangent | 53000 | each | facility | line | material | 100% | 0% | 0%
Line | Structure | Lattice Tower | 240kV | Light/Med Angle | 90000 | each | facility | line | material | 100% | 0% | 0%
Line | Structure | Lattice Tower | 240kV | Heavy Angle | 285000 | each | facility | line | material | 100% | 0% | 0%
Line | Structure | Lattice Tower | 240kV | Dead End | 307000 | each | facility | line | material | 100% | 0% | 0%
Line | Conductor | 266 | S/C | 1x | 8820 | /km | facility | line | material | 100% | 0% | 0%
Line | Conductor | 266 | S/C | 2x | 17640 | /km | facility | line | material | 100% | 0% | 0%
Line | Conductor | 266 | D/C | 1x | 17640 | /km | facility | line | material | 100% | 0% | 0%
Line | Conductor | 266 | D/C | 2x | 35280 | /km | facility | line | material | 100% | 0% | 0%
Line | Conductor | 477 | S/C | 1x | 15750 | /km | facility | line | material | 100% | 0% | 0%
Line | Conductor | 477 | S/C | 2x | 31500 | /km | facility | line | material | 100% | 0% | 0%
Line | Conductor | 477 | D/C | 1x | 31500 | /km | facility | line | material | 100% | 0% | 0%
Line | Conductor | 477 | D/C | 2x | 63000 | /km | facility | line | material | 100% | 0% | 0%
Line | Conductor | 795 | S/C | 1x | 25830 | /km | facility | line | material | 100% | 0% | 0%
Line | Conductor | 795 | S/C | 2x | 51660 | /km | facility | line | material | 100% | 0% | 0%
Line | Conductor | 795 | D/C | 1x | 51660 | /km | facility | line | material | 100% | 0% | 0%
Line | Conductor | 795 | D/C | 2x | 103320 | /km | facility | line | material | 100% | 0% | 0%
Line | Conductor | 1033 | S/C | 1x | 31500 | /km | facility | line | material | 100% | 0% | 0%
Line | Conductor | 1033 | S/C | 2x | 63000 | /km | facility | line | material | 100% | 0% | 0%
Line | Conductor | 1033 | D/C | 1x | 63000 | /km | facility | line | material | 100% | 0% | 0%
Line | Conductor | 1033 | D/C | 2x | 126000 | /km | facility | line | material | 100% | 0% | 0%
Line | Conductor | 1590 | S/C | 1x | 47250 | /km | facility | line | material | 100% | 0% | 0%
Line | Conductor | 1590 | S/C | 2x | 94500 | /km | facility | line | material | 100% | 100% | 0%
Line | Conductor | 1590 | D/C | 1x | 94500 | /km | facility | line | material | 100% | 100% | 0%
Line | Conductor | 1590 | D/C | 2x | 189000 | /km | facility | line | material | 100% | 100% | 0%
Line | Conductor | OPGW |  |  | 10300 | /km | facility | line | material | 100% | 100% | 0%
Line | Conductor | OHSW |  |  | 3090 | /km | facility | line | material | 100% | 100% | 0%
Line | Installation | Wood Pole | 138kV | Tangent | 5000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Wood Pole | 138kV | Light/Med Angle | 6250 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Wood Pole | 138kV | Heavy Angle | 8000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Wood Pole | 138kV | Dead End | 10000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Steel Pole | 138kV | Tangent | 20000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Steel Pole | 138kV | Light/Med Angle | 28000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Steel Pole | 138kV | Heavy Angle | 36000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Steel Pole | 138kV | Dead End | 44000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Steel Pole | 240kV | Tangent |  | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Steel Pole | 240kV | Light/Med Angle |  | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Steel Pole | 240kV | Heavy Angle |  | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Steel Pole | 240kV | Dead End |  | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Lattice Tower | 240kV | Tangent | 85000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Lattice Tower | 240kV | Light/Med Angle | 120000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Lattice Tower | 240kV | Heavy Angle | 370000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Lattice Tower | 240kV | Dead End | 400000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | String | 138kV | S/C | 40000 | /km | facility | line | labour | 0% | 100% | 0%
Line | Installation | String | 138kV | D/C | 50000 | /km | facility | line | labour | 0% | 100% | 0%
Line | Installation | String | 240kV | S/C | 120000 | /km | facility | line | labour | 0% | 100% | 0%
Line | Installation | String | 240kV | D/C | 150000 | /km | facility | line | labour | 0% | 100% | 0%
Line | Installation | String | OPGW |  | 10000 | /km | facility | line | labour | 0% | 100% | 0%
Line | Installation | String | OHSW |  | 7000 | /km | facility | line | labour | 0% | 100% | 0%
Line | Installation | Foundation | 240kV / Tower | Tangent | 60000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Foundation | 240kV / Tower | Light/Med Angle | 84000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Foundation | 240kV / Tower | Heavy Angle | 740000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Foundation | 240kV / Tower | Dead End | 820000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Foundation | 240kV / S/P | Tangent |  | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Foundation | 240kV / S/P | Light/Med Angle |  | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Foundation | 240kV / S/P | Heavy Angle |  | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Foundation | 240kV / S/P | Dead End |  | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Foundation | 138kV / S/P | Tangent | 5000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Foundation | 138kV / S/P | Light/Med Angle | 5000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Foundation | 138kV / S/P | Heavy Angle | 55000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Foundation | 138kV / S/P | Dead End | 60000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Foundation | 138kV / W/P | Tangent | 2000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Foundation | 138kV / W/P | Light/Med Angle | 2500 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Foundation | 138kV / W/P | Heavy Angle | 5000 | each | facility | line | labour | 0% | 100% | 0%
Line | Installation | Foundation | 138kV / W/P | Dead End | 10000 | each | facility | line | labour | 0% | 100% | 0%
Line | RoW Clearing | 138kV | Light brushing |  | 18000 | /km | facility | line | labour | 0% | 100% | 0%
Line | RoW Clearing | 138kV | Heavy brushing |  | 36000 | /km | facility | line | labour | 0% | 100% | 0%
Line | RoW Clearing | 240kV | Light brushing |  | 50000 | /km | facility | line | labour | 0% | 100% | 0%
Line | RoW Clearing | 240kV | Heavy brushing |  | 100000 | /km | facility | line | labour | 0% | 100% | 0%
Line | Rig Mat |  |  |  | 100000 | /km/90 day | facility | line | labour | 0% | 100% | 0%
Salvage | Substation Equipment | Transformer | 240kV |  | 50000 | each | facility | substation | labour | 0% | 100% | 0%
Salvage | Substation Equipment | Transformer | 138kV |  | 20000 | each | facility | substation | labour | 0% | 100% | 0%
Salvage | Substation Equipment | Circuit Break | 240kV |  | 20000 | each | facility | substation | labour | 0% | 100% | 0%
Salvage | Substation Equipment | Circuit Break | 138kV |  | 20000 | each | facility | substation | labour | 0% | 100% | 0%
Salvage | Substation Equipment | Circuit Break | 25kV |  | 10000 | each | facility | substation | labour | 0% | 100% | 0%
Salvage | Substation Equipment | Buswork | 240kV |  | 9000 | each | facility | substation | labour | 0% | 100% | 0%
Salvage | Substation Equipment | Buswork | 138kV |  | 4500 | each | facility | substation | labour | 0% | 100% | 0%
Salvage | Substation Equipment | Buswork | 25kV |  | 2500 | each | facility | substation | labour | 0% | 100% | 0%
Salvage | Line | Conductor | 240kV | S/C | 50000 | /km | facility | line | labour | 0% | 100% | 0%
Salvage | Line | Conductor | 138kV | S/C | 30000 | /km | facility | line | labour | 0% | 100% | 0%
Salvage | Line | Conductor | 240kV | D/C | 60000 | /km | facility | line | labour | 0% | 0% | 0%
Salvage | Line | Conductor | 138kV | D/C | 36000 | /km | facility | line | labour | 0% | 0% | 0%
Salvage | Line | Structure / Pole | 240kV |  | 5000 | each | facility | line | labour | 0% | 0% | 0%
Salvage | Line | Structure / Pole | 138kV |  | 2000 | each | facility | line | labour | 0% | 0% | 0%
Salvage | Line | Structure / Tower | 240kV |  | 10800 | each | facility | line | labour | 0% | 0% | 0%
Substation | Transformer | 240/138kV | 400MVA | New | 5375168 | each | facility | substation | L&M | 70% | 30% | 0%
Substation | Transformer | 240/138kV | 200MVA | New | 4139870 | each | facility | substation | L&M | 70% | 30% | 0%
Substation | Transformer | 240/138kV | 100MVA | New | 3766895 | each | facility | substation | L&M | 70% | 30% | 0%
Substation | Transformer | 138/25kV | 42MVA | New | 1901275 | each | facility | substation | L&M | 70% | 30% | 0%
Substation | Transformer | 138/25kV | 25MVA | New | 1608475 | each | facility | substation | L&M | 70% | 30% | 0%
Substation | Transformer | 500/240kV | 1200MVA | New | 3226294 | each | facility | substation | L&M | 70% | 30% | 0% |  | single phase only, 400MVA per phase
Substation | Circuit Breaker | 240kV | 1050kV | New | 441410 | each | facility | substation | L&M | 50% | 50% | 0%
Substation | Circuit Breaker | 138kV | 650kV | New | 206344 | each | facility | substation | L&M | 50% | 50% | 0%
Substation | Circuit Breaker | 25kV | 100kV | New | 133542 | each | facility | substation | L&M | 50% | 50% | 0%
Substation | Current Transformer | 240kV | 2000:1 | New | 59076 | each | facility | substation | L&M | 50% | 50% | 0% |  | cost inlcudes 3 phases as one set, applied for each CB
Substation | Current Transformer | 138kV | 1200:1 | New | 37284 | each | facility | substation | L&M | 50% | 50% | 0% |  | cost inlcudes 3 phases as one set, applied for each live tank CB, not required for dead tank CB. Generally, only ATCO adopts live tank for 144kV CB
Substation | Voltage Transformer | 240kV | 1050kV | New | 45937 | each | facility | substation | L&M | 50% | 50% | 0% |  | cost inlcudes 3 phases as one set, applied for each line termination
Substation | Voltage Transformer | 138kV | 650kV | New | 35726 | each | facility | substation | L&M | 50% | 50% | 0% |  | cost inlcudes 3 phases as one set, applied for each line termination
Substation | Potential Transformer | 240kV | 1050kV | New | 45937 | each | facility | substation | L&M | 50% | 50% | 0% |  | cost inlcudes 3 phases as one set, applied for each side of bus, e.g. 1 for north bus and 1 for south bus
Substation | Potential Transformer | 138kV | 650kV | New | 35726 | each | facility | substation | L&M | 50% | 50% | 0% |  | cost inlcudes 3 phases as one set, applied for each side of bus, e.g. 1 for north bus and 1 for south bus
Substation | VAR Cap Bank | 240kV | xMVA | New | 681306 | each | facility | substation | L&M | 50% | 50% | 0%
Substation | VAR Cap Bank | 138kV | xMVA | New | 862432 | each | facility | substation | L&M | 50% | 50% | 0%
Substation | VAR Cap Bank | 25kV | xMVA | New | 87816 | each | facility | substation | L&M | 50% | 50% | 0%
Substation | VAR Reactor | 240kV | xMVA | New | 1979015 | each | facility | substation | L&M | 50% | 50% | 0%
Substation | VAR Reactor | 138kV | xMVA | New | 1838739 | each | facility | substation | L&M | 50% | 50% | 0%
Substation | Station Service | SS transformer | 75kVA | New | 44036 | each | facility | substation | L&M | 50% | 50% | 0% |  | unique size for all new stations, one for each new sub or if there is transformer added in existing sub
Substation | Air Break | 240kV | 1050kV | New | 73617 | each | facility | substation | L&M | 50% | 50% | 0% |  | 2 per CB; 1 per bus tie if applicable; 1 per line termination; 1 per transformer
Substation | Air Break | 138kV | 650kV | New | 51736 | each | facility | substation | L&M | 50% | 50% | 0% |  | 2 per CB; 1 per bus tie if applicable; 1 per line termination; 1 per transformer
Substation | Air Break | 25kV | 100kV | New | 42812 | each | facility | substation | L&M | 50% | 50% | 0% |  | 2 per feeder
Substation | Line Termination | 240kV | 1050kV | New | 526092 | each | facility | substation | L&M | 50% | 50% | 0% |  | 1 for each line end
Substation | Line Termination | 138kV | 650kV | New | 331983 | each | facility | substation | L&M | 50% | 50% | 0% |  | 1 for each line end
Substation | Main Bus | 240kV | 4000A | New | 21375 | each | facility | substation | L&M | 50% | 50% | 0% |  | 1 main bus for each end of diameter; 1 extra main bus for each line termination
Substation | Main Bus | 138kV | 2000A | New | 10687 | each | facility | substation | L&M | 50% | 50% | 0% |  | 1 main bus for each end of diameter; 1 extra main bus for each line termination
Substation | Control Building | 4mx14m | pre-fab | New | 448546 | each | facility | substation | L&M | 50% | 50% | 0% |  | for green site
Substation | Switchgear Building | 7-cell | pre-fab | New | 639780 | each | facility | substation | L&M | 50% | 50% | 0%
Substation | Protection & Control | Relays/modules/meter | pre-fab | New | 50553 | each | facility | substation | L&M | 50% | 50% | 0% | protectionRelay.JPG | new relay or module. 4 per new transformer; 3 per new line termination; 2 per bus; 2 per group of CB, e.g. 2 for 240kV and 2 for 138kV;
Substation | Circuit Breaker | 500kV | 2000kV | New | 426520 | each | facility | substation | L&M | 50% | 50% | 0%
Substation | All sub commissioning | All sub commissioning | All sub commissioning | New | 1000 | each | facility | substation | L&M | 0% | 100% | 0% |  | last item to be estimated, 3% x "SubTotal" in $K. E.g. if the SubTotal is $2,000,000, then 3% x 2000=60
Line | 138kV_Standard | S/C | 1x477 | New (0~1km) | 1348870 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 138kV_Standard | S/C | 1x477 | New (1~10km) | 799725 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 138kV_Standard | S/C | 1x477 | New (10+km) | 433984 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 138kV_Standard | S/C | 2x477 | New (0~1km) | 1348870 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 138kV_Standard | S/C | 2x477 | New (1~10km) | 799725 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 138kV_Standard | S/C | 2x477 | New (10+km) | 433984 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 138kV_Standard | S/C | 1x266 | New (0~1km) | 1291933 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 138kV_Standard | S/C | 1x266 | New (1~10km) | 765968 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 138kV_Standard | S/C | 1x266 | New (10+km) | 415666 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 138kV_Standard | D/C | 1x477 | New (0~1km) |  | /km | facility | line | L&M | 50% | 50% | 0%
Line | 138kV_Standard | D/C | 1x477 | New (1~10km) | 1748732 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 138kV_Standard | D/C | 1x477 | New (10+km) | 1041775 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 240kV_Standard | S/C | 2x477 | New (0~1km) |  | /km | facility | line | L&M | 50% | 50% | 0%
Line | 240kV_Standard | S/C | 2x477 | New (1~10km) | 2001445 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 240kV_Standard | S/C | 2x477 | New (10+km) | 945808 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 240kV_Standard | S/C | 2(1)x795 | New (0~1km) | 2384246 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 240kV_Standard | S/C | 2(1)x795 | New (1~10km) | 1192123 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 240kV_Standard | S/C | 2(1)x795 | New (10+km) | 951140 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 240kV_Standard | D/C | 2x795 | New (0~1km) |  | /km | facility | line | L&M | 50% | 50% | 0%
Line | 240kV_Standard | D/C | 2x795 | New (1~10km) | 1167599 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 240kV_Standard | D/C | 2x795 | New (10+km) |  | /km | facility | line | L&M | 50% | 50% | 0%
Line | 240kV_Standard | D/C single side strung | 2x795 | New (0~1km) |  | /km | facility | line | L&M | 50% | 50% | 0%
Line | 240kV_Standard | D/C single side strung | 2x795 | New (1~10km) |  | /km | facility | line | L&M | 50% | 50% | 0%
Line | 240kV_Standard | D/C single side strung | 2x795 | New (10+km) | 1665561 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 240kV_Standard | D/C | 2x1033 | New | 2439694 | /km | facility | line | L&M | 50% | 50% | 0%
Line | 500kV_Standard | S/C | 2X1033 | New |  | /km | facility | line | L&M | 50% | 50% | 0%
Telecom | Equipment | Equipment/Building |  | New | 58437 | Lot | facility | telecom | L&M | 50% | 50% | 0%
Telecom | Fiber |  |  | New | 29205 | Lot | facility | telecom | L&M | 50% | 50% | 0%
Telecom | Tower&Radio | Steel |  | New | 121461 | each | facility | telecom | L&M | 50% | 50% | 0%
Distributed | Project Management | Project Management |  |  | 7.4% |  | non-facility | Disrtibuted | labour | 0% | 100% | 0%
Distributed | Construction Management | Construction Management |  |  | 5.6% |  | non-facility | Disrtibuted | labour | 0% | 100% | 0%
Distributed | Contingency | Contingency |  |  | 15.7% |  | non-facility | Disrtibuted | other | 0% | 0% | 100%
Owners | Proposal to Provide Service | Proposal to Provide Service |  |  | 3% |  | non-facility | Owners | labour | 0% | 100% | 0%
Owners | Facility Application | Facility Application |  |  | 3% |  | non-facility | Owners | labour | 0% | 100% | 0%
Owners | Land related cost | Land related cost |  |  | 3% |  | non-facility | Owners | labour | 0% | 100% | 0%
Other | AFUDC | AFUDC |  |  | 6.9% |  | non-facility | Other | other | 0% | 0% | 100%
Other | E&S | E&S |  |  | 6.9% |  | non-facility | Other | labour | 0% | 100% | 0%

## Cashflow
CF_ID | CF_TYPE | fclty_tpe | voltage | class | Yr1 | Yr2 | Yr3 | Yr4 | Yr5 | Total
1 | Line _ 138kV _ 0-10km | Line | 138kV | 0-10km | 100% |  |  |  |  | 100%
2 | Line _ 138kV _ 11-50km | Line | 138kV | 11-50km | 80% | 20% |  |  |  | 100%
3 | Line _ 138kV _ 51-100km | Line | 138kV | 51-100km | 20% | 70% | 10% |  |  | 100%
4 | Line _ 138kV _ 100km+ | Line | 138kV | 100km+ | 20% | 35% | 35% | 10% |  | 100%
5 | Line _ 240kV _ 0-10km | Line | 240kV | 0-10km | 20% | 80% |  |  |  | 100%
6 | Line _ 240kV _ 11-50km | Line | 240kV | 11-50km | 20% | 70% | 10% |  |  | 100%
7 | Line _ 240kV _ 51-100km | Line | 240kV | 51-100km | 20% | 35% | 35% | 10% |  | 100%
8 | Line _ 240kV _ 100km+ | Line | 240kV | 100km+ | 20% | 45% | 18% | 17% |  | 100%
9 | Line _ 500kV _ 51-100km | Line | 500kV | 51-100km | 20% | 35% | 35% | 10% |  | 100%
10 | Line _ 500kV _ 100km+ | Line | 500kV | 100km+ | 20% | 35% | 25% | 10% | 10% | 100%
11 | Substation _ 138kV _ $0-$5M | Substation | 138kV | $0-$5M | 100% |  |  |  |  | 100%
12 | Substation _ 138kV _ $5M-$10M | Substation | 138kV | $5M-$10M | 80% | 20% |  |  |  | 100%
13 | Substation _ 138kV _ $10M-$20M | Substation | 138kV | $10M-$20M | 25% | 70% | 5% |  |  | 100%
14 | Substation _ 138kV _ $20M+ | Substation | 138kV | $20M+ | 35% | 55% | 10% |  |  | 100%
15 | Substation _ 240kV _ $0-$5M | Substation | 240kV | $0-$5M | 100% |  |  |  |  | 100%
16 | Substation _ 240kV _ $5M-$10M | Substation | 240kV | $5M-$10M | 80% | 20% |  |  |  | 100%
17 | Substation _ 240kV _ $10M-$20M | Substation | 240kV | $10M-$20M | 25% | 70% | 5% |  |  | 100%
18 | Substation _ 240kV _ $20M+ | Substation | 240kV | $20M+ | 35% | 55% | 10% |  |  | 100%

## Inflation
year | inflation | ref_year
2000 | 2%
2001 | 2%
2002 | 2%
2003 | 2%
2004 | 2%
2005 | 2%
2006 | 2%
2007 | 2%
2008 | 2%
2009 | 2%
2010 | 2%
2011 | 2% | 1
2012 | 2%
2013 | 2%
2014 | 2%
2015 | 2%
2016 | 2%
2017 | 2%
2018 | 2%
2019 | 2%
2020 | 2%
2021 | 2%
2022 | 2%
2023 | 2%
2024 | 2%
2025 | 2%
2026 | 2%
2027 | 2%
2028 | 2%
2029 | 2%
2030 | 2%
2031 | 2%
2032 | 2%
2033 | 2%
2034 | 2%
2035 | 2%
2036 | 2%
2037 | 2%
2038 | 2%
2039 | 2%
2040 | 2%