## UnitCost
Level 1 | Level 2 | Level 3 | Level 4 | Level 5 | Unit Price | Unit | group_1 | group_2 | group_3 | Material | Labour | Other | User Guide
Substation | Transformer | 138/25kV | 25MVA | Equipment | 917461 | each | facility | substation | material | 100% | 0% | 0% |  | 917461 | TRUE
Substation | Transformer | 138/25kV | 42MVA | Equipment | 1084471 | each | facility | substation | material | 100% | 0% | 0% |  | 1084471 | TRUE
Substation | Transformer | 240/138kV | 100MVA | Equipment | 2148604 | each | facility | substation | material | 100% | 0% | 0% |  | 2148604 | TRUE
Substation | Transformer | 240/138kV | 200MVA | Equipment | 2361346 | each | facility | substation | material | 100% | 0% | 0% |  | 2361346 | TRUE
Substation | Transformer | 240/138kV | 400MVA | Equipment | 3065949 | each | facility | substation | material | 100% | 0% | 0% |  | 3065949 | TRUE
Substation | Transformer | 500/240kV | 1200MVA | Equipment | 1840250 | each | facility | substation | material | 100% | 0% | 0% | single phase only, 400MVA per phase | 1840250 | TRUE
Substation | Circuit Breaker | 240kV | 1050kV | Equipment | 220201 | each | facility | substation | material | 100% | 0% | 0% |  | 220201 | TRUE
Substation | Circuit Breaker | 138kV | 650kV | Equipment | 102936 | each | facility | substation | material | 100% | 0% | 0% |  | 102936 | TRUE
Substation | Circuit Breaker | 25kV | 100kV | Equipment | 66618 | each | facility | substation | material | 100% | 0% | 0% |  | 66618 | TRUE
Substation | Current Transformer | 240kV | 2000:1 | Equipment | 29470 | each | facility | substation | material | 100% | 0% | 0% |  | 29470 | TRUE
Substation | Current Transformer | 138kV | 1200:1 | Equipment | 18599 | each | facility | substation | material | 100% | 0% | 0% |  | 18599 | TRUE
Substation | Voltage Transformer | 240kV | 1050kV | Equipment | 22916 | each | facility | substation | material | 100% | 0% | 0% |  | 22916 | TRUE
Substation | Voltage Transformer | 138kV | 650kV | Equipment | 17822 | each | facility | substation | material | 100% | 0% | 0% |  | 17822 | TRUE
Substation | Potential Transformer | 240kV | 1050kV | Equipment | 22916 | each | facility | substation | material | 100% | 0% | 0% |  | 22916 | TRUE
Substation | Potential Transformer | 138kV | 650kV | Equipment | 17822 | each | facility | substation | material | 100% | 0% | 0% |  | 17822 | TRUE
Substation | VAR Cap Bank | 240kV | xMVA | Equipment | 453511 | each | facility | substation | material | 100% | 0% | 0% |  | 453511 | TRUE
Substation | VAR Cap Bank | 138kV | xMVA | Equipment | 574078 | each | facility | substation | material | 100% | 0% | 0% |  | 574078 | TRUE
Substation | VAR Cap Bank | 25kV | xMVA | Equipment | 58455 | each | facility | substation | material | 100% | 0% | 0% |  | 58455 | TRUE
Substation | VAR Reactor | 240kV | xMVA | Equipment | 1437620 | each | facility | substation | material | 100% | 0% | 0% |  | 1437620 | TRUE
Substation | VAR Reactor | 138kV | xMVA | Equipment | 1335719 | each | facility | substation | material | 100% | 0% | 0% |  | 1335719 | TRUE
Substation | Station Service | S.S transformer | 75KVA | Equipment | 31989 | each | facility | substation | material | 100% | 0% | 0% |  | 31989 | TRUE
Substation | Air Break | 240kV | 1050kV | Equipment | 36724 | each | facility | substation | material | 100% | 0% | 0% |  | 36724 | TRUE
Substation | Air Break | 138kV | 650kV | Equipment | 25809 | each | facility | substation | material | 100% | 0% | 0% |  | 25809 | TRUE
Substation | Air Break | 25kV | 100kV | Equipment | 21357 | each | facility | substation | material | 100% | 0% | 0% |  | 21357 | TRUE
Substation | Line Termination | 240kV | 1050kV | Equipment | 350193 | each | facility | substation | material | 100% | 0% | 0% |  | 350193 | TRUE
Substation | Line Termination | 138kV | 650kV | Equipment | 220984 | each | facility | substation | material | 100% | 0% | 0% |  | 220984 | TRUE
Substation | Main Bus | 240kV | 4000A | Equipment | 10663 | each | facility | substation | material | 100% | 0% | 0% |  | 10663 | TRUE
Substation | Main Bus | 138kV | 2000A | Equipment | 5332 | each | facility | substation | material | 100% | 0% | 0% |  | 5332 | TRUE
Substation | Control Building | 4mx14m | pre-fab | Equipment | 298575 | each | facility | substation | material | 100% | 0% | 0% |  | 298575 | TRUE
Substation | Switchgear Building | 7-cell | pre-fab | Equipment | 639780 | each | facility | substation | material | 100% | 0% | 0% | applicable for addition or substraction cells | 100000 | FALSE
Substation | Protection relays/modules |  |  | Equipment | 33650 | each | facility | substation | material | 100% | 0% | 0% |  | 33650 | TRUE
Substation | Control cables | AWG #10 and below | pre-fab | Equipment | 11 | /m | facility | substation | material | 100% | 0% | 0% | 600m/relay or module; AWG #10 and below | 11 | TRUE
Substation | Transformer | 138/25kV | 25MVA | Installation | 345507 | each | facility | substation | labour | 0% | 0% | 0% |  | 345507 | TRUE
Substation | Transformer | 138/25kV | 42MVA | Installation | 408402 | each | facility | substation | labour | 0% | 100% | 0% |  | 408402 | TRUE
Substation | Transformer | 240/138kV | 100MVA | Installation | 809145 | each | facility | substation | labour | 0% | 100% | 0% |  | 809145 | TRUE
Substation | Transformer | 240/138kV | 200MVA | Installation | 889262 | each | facility | substation | labour | 0% | 100% | 0% |  | 889262 | TRUE
Substation | Transformer | 240/138kV | 400MVA | Installation | 1154609 | each | facility | substation | labour | 0% | 100% | 0% |  | 1154609 | TRUE
Substation | Transformer | 500/240kV | 1200MVA | Installation | 693022 | each | facility | substation | labour | 0% | 100% | 0% | single phase only, 400MVA per phase | 693022 | TRUE
Substation | Circuit Breaker | 240kV | 1050kV | Installation | 110605 | each | facility | substation | labour | 0% | 100% | 0% |  | 110605 | TRUE
Substation | Circuit Breaker | 138kV | 650kV | Installation | 51704 | each | facility | substation | labour | 0% | 100% | 0% |  | 51704 | TRUE
Substation | Circuit Breaker | 25kV | 100kV | Installation | 33462 | each | facility | substation | labour | 0% | 100% | 0% |  | 33462 | TRUE
Substation | Current Transformer | 240kV | 2000:1 | Installation | 14803 | each | facility | substation | labour | 0% | 100% | 0% |  | 14803 | TRUE
Substation | Current Transformer | 138kV | 1200:1 | Installation | 9342 | each | facility | substation | labour | 0% | 100% | 0% |  | 9342 | TRUE
Substation | Voltage Transformer | 240kV | 1050kV | Installation | 11510 | each | facility | substation | labour | 0% | 100% | 0% |  | 11510 | TRUE
Substation | Voltage Transformer | 138kV | 650kV | Installation | 8952 | each | facility | substation | labour | 0% | 100% | 0% |  | 8952 | TRUE
Substation | Potential Transformer | 240kV | 1050kV | Installation | 11510 | each | facility | substation | labour | 0% | 100% | 0% |  | 11510 | TRUE
Substation | Potential Transformer | 138kV | 650kV | Installation | 8952 | each | facility | substation | labour | 0% | 100% | 0% |  | 8952 | TRUE
Substation | VAR Cap Bank | 240kV | xMVA | Installation | 227795 | each | facility | substation | labour | 0% | 100% | 0% |  | 227795 | TRUE
Substation | VAR Cap Bank | 138kV | xMVA | Installation | 288354 | each | facility | substation | labour | 0% | 100% | 0% |  | 288354 | TRUE
Substation | VAR Cap Bank | 25kV | xMVA | Installation | 29361 | each | facility | substation | labour | 0% | 100% | 0% |  | 29361 | TRUE
Substation | VAR Reactor | 240kV | xMVA | Installation | 541395 | each | facility | substation | labour | 0% | 100% | 0% |  | 541395 | TRUE
Substation | VAR Reactor | 138kV | xMVA | Installation | 503020 | each | facility | substation | labour | 0% | 100% | 0% |  | 503020 | TRUE
Substation | Station Service | S.S transformer | 75KVA | Installation | 12047 | each | facility | substation | labour | 0% | 100% | 0% |  | 12047 | TRUE
Substation | Air Break | 240kV | 1050kV | Installation | 18446 | each | facility | substation | labour | 0% | 100% | 0% |  | 18446 | TRUE
Substation | Air Break | 138kV | 650kV | Installation | 12963 | each | facility | substation | labour | 0% | 100% | 0% |  | 12963 | TRUE
Substation | Air Break | 25kV | 100kV | Installation | 10727 | each | facility | substation | labour | 0% | 100% | 0% |  | 10727 | TRUE
Substation | Line Termination | 240kV | 1050kV | Installation | 175899 | each | facility | substation | labour | 0% | 100% | 0% |  | 175899 | TRUE
Substation | Line Termination | 138kV | 650kV | Installation | 110998 | each | facility | substation | labour | 0% | 100% | 0% |  | 110998 | TRUE
Substation | Main Bus | 240kV | 4000A | Installation | 5356 | each | facility | substation | labour | 0% | 100% | 0% |  | 5356 | TRUE
Substation | Main Bus | 138kV | 2000A | Installation | 2678 | each | facility | substation | labour | 0% | 100% | 0% |  | 2678 | TRUE
Substation | Control Building | 4mx14m | pre-fab | Installation | 149971 | each | facility | substation | labour | 0% | 100% | 0% |  | 149971 | TRUE
Substation | Switchgear Building | 7-cell | pre-fab | Installation | $ - | each | facility | substation | labour | 0% | 100% | 0% |  | 16902 | FALSE
Substation | Protection relays/modules |  |  | Installation | 16902 | each | facility | substation | labour | 0% | 100% | 0% |  | 53 | FALSE
Substation | Control cables | AWG #10 and below | trenching/closing | Installation | 53 | /m | facility | substation | labour | 0% | 100% | 0% |  | 345507 | FALSE
Substation | Transformer | 138/25kV | 25MVA | Foundation | 345507 | each | facility | substation | labour | 0% | 100% | 0% |  | 408402 | FALSE
Substation | Transformer | 138/25kV | 42MVA | Foundation | 408402 | each | facility | substation | labour | 0% | 100% | 0% |  | 809145 | FALSE
Substation | Transformer | 240/138kV | 100MVA | Foundation | 809145 | each | facility | substation | labour | 0% | 100% | 0% |  | 889262 | FALSE
Substation | Transformer | 240/138kV | 200MVA | Foundation | 889262 | each | facility | substation | labour | 0% | 100% | 0% |  | 1154609 | FALSE
Substation | Transformer | 240/138kV | 400MVA | Foundation | 1154609 | each | facility | substation | labour | 0% | 100% | 0% | single phase only, 400MVA per phase | 693022 | FALSE
Substation | Transformer | 500/240kV | 1200MVA | Foundation | 693022 | each | facility | substation | labour | 0% | 100% | 0% |  | 110605 | FALSE
Substation | Circuit Breaker | 240kV | 1050kV | Foundation | 110605 | each | facility | substation | labour | 0% | 100% | 0% |  | 51704 | FALSE
Substation | Circuit Breaker | 138kV | 650kV | Foundation | 51704 | each | facility | substation | labour | 0% | 100% | 0% |  | 33462 | FALSE
Substation | Circuit Breaker | 25kV | 100kV | Foundation | 33462 | each | facility | substation | labour | 0% | 100% | 0% |  | 14803 | FALSE
Substation | Current Transformer | 240kV | 2000:1 | Foundation | 14803 | each | facility | substation | labour | 0% | 100% | 0% |  | 9342 | FALSE
Substation | Current Transformer | 138kV | 1200:1 | Foundation | 9342 | each | facility | substation | labour | 0% | 100% | 0% |  | 11510 | FALSE
Substation | Voltage Transformer | 240kV | 1050kV | Foundation | 11510 | each | facility | substation | labour | 0% | 100% | 0% |  | 8952 | FALSE
Substation | Voltage Transformer | 138kV | 650kV | Foundation | 8952 | each | facility | substation | labour | 0% | 100% | 0% |  | 11510 | FALSE
Substation | Potential Transformer | 240kV | 1050kV | Foundation | 11510 | each | facility | substation | labour | 0% | 100% | 0% |  | 8952 | FALSE
Substation | Potential Transformer | 138kV | 650kV | Foundation | 8952 | each | facility | substation | labour | 0% | 100% | 0% |  | $ - | FALSE
Substation | VAR Cap Bank | 240kV | xMVA | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0% |  | $ - | TRUE
Substation | VAR Cap Bank | 138kV | xMVA | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0% |  | $ - | TRUE
Substation | VAR Cap Bank | 25kV | xMVA | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0% |  | $ - | TRUE
Substation | VAR Reactor | 240kV | xMVA | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0% |  | $ - | TRUE
Substation | VAR Reactor | 138kV | xMVA | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0% |  | $ - | TRUE
Substation | Station Service | S.S transformer | 75KVA | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0% |  | 18446 | FALSE
Substation | Air Break | 240kV | 1050kV | Foundation | 18446 | each | facility | substation | labour | 0% | 100% | 0% |  | 12963 | FALSE
Substation | Air Break | 138kV | 650kV | Foundation | 12963 | each | facility | substation | labour | 0% | 100% | 0% |  | 10727 | FALSE
Substation | Air Break | 25kV | 100kV | Foundation | 10727 | each | facility | substation | labour | 0% | 100% | 0% |  | $ - | FALSE
Substation | Line Termination | 240kV | 1050kV | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0% |  | $ - | TRUE
Substation | Line Termination | 138kV | 650kV | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0% |  | 5356 | FALSE
Substation | Main Bus | 240kV | 4000A | Foundation | 5356 | each | facility | substation | labour | 0% | 100% | 0% |  | 2678 | FALSE
Substation | Main Bus | 138kV | 2000A | Foundation | 2678 | each | facility | substation | labour | 0% | 100% | 0% |  | $ - | FALSE
Substation | Control Building | 4mx14m | pre-fab | Foundation | $ - | each | facility | substation | labour |  | 100% | 0% | station sizing guide: new 240kV sub, 150mx135m; new 138kV sub, 135mx75m; new 240kV switching sub, 100mx100m; new 138kV switching sub, 75mx75m; 240kV site expansion, 20mx20m per major eqpmt; 138kV site expansion, 15mx15m per major eqpmt incl. excavation/backfill, fence and gate | 260 | FALSE
Substation | Switchgear Building | 7-cell | pre-fab | Foundation | $ - | each | facility | substation | labour | 0% | 100% | 0% | default length for new station is 100m, or as per measurement on map, whichever is available | 1066 | FALSE
Substation | Site Development |  |  |  | 260 | /m² | facility | substation | labour | 0% | 100% | 0% |  | 3000 | FALSE
Substation | Access road (7m) |  |  |  | 1066 | /m | facility | substation | labour | 0% | 100% | 0% |  | 4500 | FALSE
Line | Structure | Wood Pole | 138kV | Tangent | 3000 | each | facility | line | material | 100% | 100% | 0% |  | 5500 | FALSE
Line | Structure | Wood Pole | 138kV | Light/Med Angle | 4500 | each | facility | line | material | 100% | 100% | 0% |  | 10000 | FALSE
Line | Structure | Wood Pole | 138kV | Heavy Angle | 5500 | each | facility | line | material | 100% | 100% | 0% |  | 22000 | FALSE
Line | Structure | Wood Pole | 138kV | Dead End | 10000 | each | facility | line | material | 100% | 100% | 0% |  | 30000 | FALSE
Line | Structure | Steel Pole | 138kV | Tangent | 22000 | each | facility | line | material | 100% | 0% | 0% |  | 39000 | FALSE
Line | Structure | Steel Pole | 138kV | Light/Med Angle | 30000 | each | facility | line | material | 100% | 0% | 0% |  | 47000 | FALSE
Line | Structure | Steel Pole | 138kV | Heavy Angle | 39000 | each | facility | line | material | 100% | 0% | 0% |  | 20000 | FALSE
Line | Structure | Steel Pole | 138kV | Dead End | 47000 | each | facility | line | material | 100% | 0% | 0% |  | 50000 | FALSE
Line | Structure | Steel Pole | 240kV | Tangent | 20000 | each | facility | line | material | 100% | 0% | 0% |  | 190000 | FALSE
Line | Structure | Steel Pole | 240kV | Light/Med Angle | 50000 | each | facility | line | material | 100% | 0% | 0% |  | 205000 | FALSE
Line | Structure | Steel Pole | 240kV | Heavy Angle | 190000 | each | facility | line | material | 100% | 0% | 0% |  | 53000 | FALSE
Line | Structure | Steel Pole | 240kV | Dead End | 205000 | each | facility | line | material | 100% | 0% | 0% |  | 90000 | FALSE
Line | Structure | Lattice Tower | 240kV | Tangent | 53000 | each | facility | line | material | 100% | 0% | 0% |  | 285000 | FALSE
Line | Structure | Lattice Tower | 240kV | Light/Med Angle | 90000 | each | facility | line | material | 100% | 0% | 0% |  | 307000 | FALSE
Line | Structure | Lattice Tower | 240kV | Heavy Angle | 285000 | each | facility | line | material | 100% | 0% | 0% |  | 8820 | FALSE
Line | Structure | Lattice Tower | 240kV | Dead End | 307000 | each | facility | line | material | 100% | 0% | 0% |  | 17640 | FALSE
Line | Conductor | 266 | S/C | 1x | 8820 | /km | facility | line | material | 100% | 0% | 0% |  | 17640 | FALSE
Line | Conductor | 266 | S/C | 2x | 17640 | /km | facility | line | material | 100% | 0% | 0% |  | 35280 | FALSE
Line | Conductor | 266 | D/C | 1x | 17640 | /km | facility | line | material | 100% | 0% | 0% |  | 15750 | FALSE
Line | Conductor | 266 | D/C | 2x | 35280 | /km | facility | line | material | 100% | 0% | 0% |  | 31500 | FALSE
Line | Conductor | 477 | S/C | 1x | 15750 | /km | facility | line | material | 100% | 0% | 0% |  | 31500 | FALSE
Line | Conductor | 477 | S/C | 2x | 31500 | /km | facility | line | material | 100% | 0% | 0% |  | 63000 | FALSE
Line | Conductor | 477 | D/C | 1x | 31500 | /km | facility | line | material | 100% | 0% | 0% |  | 25830 | FALSE
Line | Conductor | 477 | D/C | 2x | 63000 | /km | facility | line | material | 100% | 0% | 0% |  | 51660 | FALSE
Line | Conductor | 795 | S/C | 1x | 25830 | /km | facility | line | material | 100% | 0% | 0% |  | 51660 | FALSE
Line | Conductor | 795 | S/C | 2x | 51660 | /km | facility | line | material | 100% | 0% | 0% |  | 103320 | FALSE
Line | Conductor | 795 | D/C | 1x | 51660 | /km | facility | line | material | 100% | 0% | 0% |  | 31500 | FALSE
Line | Conductor | 795 | D/C | 2x | 103320 | /km | facility | line | material | 100% | 0% | 0% |  | 63000 | FALSE
Line | Conductor | 1033 | S/C | 1x | 31500 | /km | facility | line | material | 100% | 0% | 0% |  | 63000 | FALSE
Line | Conductor | 1033 | S/C | 2x | 63000 | /km | facility | line | material | 100% | 0% | 0% |  | 126000 | FALSE
Line | Conductor | 1033 | D/C | 1x | 63000 | /km | facility | line | material | 100% | 0% | 0% |  | 47250 | FALSE
Line | Conductor | 1033 | D/C | 2x | 126000 | /km | facility | line | material | 100% | 0% | 0% |  | 94500 | FALSE
Line | Conductor | 1590 | S/C | 1x | 47250 | /km | facility | line | material | 100% | 0% | 0% |  | 94500 | FALSE
Line | Conductor | 1590 | S/C | 2x | 94500 | /km | facility | line | material | 100% | 100% | 0% |  | 189000 | FALSE
Line | Conductor | 1590 | D/C | 1x | 94500 | /km | facility | line | material | 100% | 100% | 0% |  | 10300 | FALSE
Line | Conductor | 1590 | D/C | 2x | 189000 | /km | facility | line | material | 100% | 100% | 0% |  | 3090 | FALSE
Line | Conductor | OPGW |  |  | 10300 | /km | facility | line | material | 100% | 100% | 0% |  | 5000 | FALSE
Line | Conductor | OHSW |  |  | 3090 | /km | facility | line | material | 100% | 100% | 0% |  | 6250 | FALSE
Line | Installation | Wood Pole | 138kV | Tangent | 5000 | each | facility | line | labour | 0% | 100% | 0% |  | 8000 | FALSE
Line | Installation | Wood Pole | 138kV | Light/Med Angle | 6250 | each | facility | line | labour | 0% | 100% | 0% |  | 10000 | FALSE
Line | Installation | Wood Pole | 138kV | Heavy Angle | 8000 | each | facility | line | labour | 0% | 100% | 0% |  | 20000 | FALSE
Line | Installation | Wood Pole | 138kV | Dead End | 10000 | each | facility | line | labour | 0% | 100% | 0% |  | 28000 | FALSE
Line | Installation | Steel Pole | 138kV | Tangent | 20000 | each | facility | line | labour | 0% | 100% | 0% |  | 36000 | FALSE
Line | Installation | Steel Pole | 138kV | Light/Med Angle | 28000 | each | facility | line | labour | 0% | 100% | 0% |  | 44000 | FALSE
Line | Installation | Steel Pole | 138kV | Heavy Angle | 36000 | each | facility | line | labour | 0% | 100% | 0% |  |  | FALSE
Line | Installation | Steel Pole | 138kV | Dead End | 44000 | each | facility | line | labour | 0% | 100% | 0% |  |  | FALSE
Line | Installation | Steel Pole | 240kV | Tangent |  | each | facility | line | labour | 0% | 100% | 0% |  |  | TRUE
Line | Installation | Steel Pole | 240kV | Light/Med Angle |  | each | facility | line | labour | 0% | 100% | 0% |  |  | TRUE
Line | Installation | Steel Pole | 240kV | Heavy Angle |  | each | facility | line | labour | 0% | 100% | 0% |  | 85000 | FALSE
Line | Installation | Steel Pole | 240kV | Dead End |  | each | facility | line | labour | 0% | 100% | 0% |  | 120000 | FALSE
Line | Installation | Lattice Tower | 240kV | Tangent | 85000 | each | facility | line | labour | 0% | 100% | 0% |  | 370000 | FALSE
Line | Installation | Lattice Tower | 240kV | Light/Med Angle | 120000 | each | facility | line | labour | 0% | 100% | 0% |  | 400000 | FALSE
Line | Installation | Lattice Tower | 240kV | Heavy Angle | 370000 | each | facility | line | labour | 0% | 100% | 0% |  | 40000 | FALSE
Line | Installation | Lattice Tower | 240kV | Dead End | 400000 | each | facility | line | labour | 0% | 100% | 0% |  | 50000 | FALSE
Line | Installation | String | 138kV | S/C | 40000 | /km | facility | line | labour | 0% | 100% | 0% |  | 120000 | FALSE
Line | Installation | String | 138kV | D/C | 50000 | /km | facility | line | labour | 0% | 100% | 0% |  | 150000 | FALSE
Line | Installation | String | 240kV | S/C | 120000 | /km | facility | line | labour | 0% | 100% | 0% |  | 10000 | FALSE
Line | Installation | String | 240kV | D/C | 150000 | /km | facility | line | labour | 0% | 100% | 0% |  | 7000 | FALSE
Line | Installation | String | OPGW |  | 10000 | /km | facility | line | labour | 0% | 100% | 0% |  | 60000 | FALSE
Line | Installation | String | OHSW |  | 7000 | /km | facility | line | labour | 0% | 100% | 0% |  | 84000 | FALSE
Line | Installation | Foundation | 240kV / Tower | Tangent | 60000 | each | facility | line | labour | 0% | 100% | 0% |  | 740000 | FALSE
Line | Installation | Foundation | 240kV / Tower | Light/Med Angle | 84000 | each | facility | line | labour | 0% | 100% | 0% |  | 820000 | FALSE
Line | Installation | Foundation | 240kV / Tower | Heavy Angle | 740000 | each | facility | line | labour | 0% | 100% | 0% |  |  | FALSE
Line | Installation | Foundation | 240kV / Tower | Dead End | 820000 | each | facility | line | labour | 0% | 100% | 0% |  |  | FALSE
Line | Installation | Foundation | 240kV / S/P | Tangent |  | each | facility | line | labour | 0% | 100% | 0% |  |  | TRUE
Line | Installation | Foundation | 240kV / S/P | Light/Med Angle |  | each | facility | line | labour | 0% | 100% | 0% |  |  | TRUE
Line | Installation | Foundation | 240kV / S/P | Heavy Angle |  | each | facility | line | labour | 0% | 100% | 0% |  | 5000 | FALSE
Line | Installation | Foundation | 240kV / S/P | Dead End |  | each | facility | line | labour | 0% | 100% | 0% |  | 5000 | FALSE
Line | Installation | Foundation | 138kV / S/P | Tangent | 5000 | each | facility | line | labour | 0% | 100% | 0% |  | 55000 | FALSE
Line | Installation | Foundation | 138kV / S/P | Light/Med Angle | 5000 | each | facility | line | labour | 0% | 100% | 0% |  | 60000 | FALSE
Line | Installation | Foundation | 138kV / S/P | Heavy Angle | 55000 | each | facility | line | labour | 0% | 100% | 0% |  | 2000 | FALSE
Line | Installation | Foundation | 138kV / S/P | Dead End | 60000 | each | facility | line | labour | 0% | 100% | 0% |  | 2500 | FALSE
Line | Installation | Foundation | 138kV / W/P | Tangent | 2000 | each | facility | line | labour | 0% | 100% | 0% |  | 5000 | FALSE
Line | Installation | Foundation | 138kV / W/P | Light/Med Angle | 2500 | each | facility | line | labour | 0% | 100% | 0% |  | 10000 | FALSE
Line | Installation | Foundation | 138kV / W/P | Heavy Angle | 5000 | each | facility | line | labour | 0% | 100% | 0% |  | 18000 | FALSE
Line | Installation | Foundation | 138kV / W/P | Dead End | 10000 | each | facility | line | labour | 0% | 100% | 0% |  | 36000 | FALSE
Line | R/W Clearing | 138kV | Light brushing |  | 18000 | /km | facility | line | labour | 0% | 100% | 0% |  | 50000 | FALSE
Line | R/W Clearing | 138kV | Heavy brushing |  | 36000 | /km | facility | line | labour | 0% | 100% | 0% |  | 100000 | FALSE
Line | R/W Clearing | 240kV | Light brushing |  | 50000 | /km | facility | line | labour | 0% | 100% | 0% |  | 100000 | FALSE
Line | R/W Clearing | 240kV | Heavy brushing |  | 100000 | /km | facility | line | labour | 0% | 100% | 0% |  | 50000 | FALSE
Line | Rig Mat |  |  |  | 100000 | /km/90 day | facility | line | labour | 0% | 100% | 0% |  | 20000 | FALSE
Salvage | Substation Equipment | Transformer | 240kV |  | 50000 | each | facility | substation | labour | 0% | 100% | 0% |  | 20000 | FALSE
Salvage | Substation Equipment | Transformer | 138kV |  | 20000 | each | facility | substation | labour | 0% | 100% | 0% |  | 20000 | TRUE
Salvage | Substation Equipment | Circuit Break | 240kV |  | 20000 | each | facility | substation | labour | 0% | 100% | 0% |  | 10000 | FALSE
Salvage | Substation Equipment | Circuit Break | 138kV |  | 20000 | each | facility | substation | labour | 0% | 100% | 0% |  | 9000 | FALSE
Salvage | Substation Equipment | Circuit Break | 25kV |  | 10000 | each | facility | substation | labour | 0% | 100% | 0% |  | 4500 | FALSE
Salvage | Substation Equipment | Buswork Equipment | 240kV |  | 9000 | each | facility | substation | labour | 0% | 100% | 0% |  | 2500 | FALSE
Salvage | Substation Equipment | Buswork Equipment | 138kV |  | 4500 | each | facility | substation | labour | 0% | 100% | 0% |  | 50000 | FALSE
Salvage | Substation Equipment | Buswork Equipment | 25kV |  |  | each | facility | substation | labour | 0% | 100% | 0% |  | 30000 | FALSE
Salvage | Substation Equipment |  |  |  |  | each | facility | substation | labour | 0% | 100% | 0% |  | 60000 | FALSE
Salvage | Substation Equipment |  |  |  |  | each | facility | substation | labour | 0% | 100% | 0% |  | 36000 | FALSE
Salvage | Substation Equipment |  |  |  |  | each | facility | substation | labour | 0% | 100% | 0% |  | 5000 | FALSE
Salvage | Substation Equipment |  |  |  |  | each | facility | substation | labour | 0% | 100% | 0% |  | 2000 | FALSE
Salvage | Line | Conductor | 240kV | S/C | 50000 | /km | facility | line | labour | 0% | 100% | 0% |  | 10800 | FALSE
Salvage | Line | Conductor | 138kV | S/C | 30000 | /km | facility | line | labour | 0% | 100% | 0% |  | 5375168 | FALSE
Salvage | Line | Conductor | 240kV | D/C | 60000 | /km | facility | line | labour | 0% | 0% | 0% |  | 4139870 | FALSE
Salvage | Line | Conductor | 138kV | D/C | 36000 | /km | facility | line | labour | 0% | 0% | 0% |  | 3766895 | FALSE
Salvage | Line | Structure / Pole | 240kV |  | 5000 | each | facility | line | labour | 0% | 0% | 0% |  | 1901275 | FALSE
Salvage | Line | Structure / Pole | 138kV |  | 2000 | each | facility | line | labour | 0% | 0% | 0% |  | 1608475 | FALSE
Salvage | Line | Structure / Tower | 240kV |  | 10800 | each | facility | line | labour | 0% | 0% | 0% | single phase only, 400MVA per phase | 3226294 | FALSE
Substation | Transformer | 240/138kV | 400MVA | New | 5375168 | each | facility | substation | L&M | 70% | 30% | 0% |  | 441410 | FALSE
Substation | Transformer | 240/138kV | 200MVA | New | 4139870 | each | facility | substation | L&M | 70% | 30% | 0% |  | 206344 | FALSE
Substation | Transformer | 240/138kV | 100MVA | New | 3766895 | each | facility | substation | L&M | 70% | 30% | 0% |  | 133542 | FALSE
Substation | Transformer | 138/25kV | 42MVA | New | 1901275 | each | facility | substation | L&M | 70% | 30% | 0% | cost inlcudes 3 phases as one set, applied for each CB | 59076 | FALSE
Substation | Transformer | 138/25kV | 25MVA | New | 1608475 | each | facility | substation | L&M | 70% | 30% | 0% | cost inlcudes 3 phases as one set, applied for each live tank CB, not required for dead tank CB. Generally, only ATCO adopts live tank for 144kV CB | 37284 | FALSE
Substation | Transformer | 500/240kV | 1200MVA | New | 3226294 | each | facility | substation | L&M | 70% | 30% | 0% | cost inlcudes 3 phases as one set, applied for each line termination | 45937 | FALSE
Substation | Circuit Breaker | 240kV | 1050kV | New | 441410 | each | facility | substation | L&M | 50% | 50% | 0% | cost inlcudes 3 phases as one set, applied for each line termination | 35726 | FALSE
Substation | Circuit Breaker | 138kV | 650kV | New | 206344 | each | facility | substation | L&M | 50% | 50% | 0% | cost inlcudes 3 phases as one set, applied for each side of bus, e.g. 1 for north bus and 1 for south bus | 45937 | FALSE
Substation | Circuit Breaker | 25kV | 100kV | New | 133542 | each | facility | substation | L&M | 50% | 50% | 0% | cost inlcudes 3 phases as one set, applied for each side of bus, e.g. 1 for north bus and 1 for south bus | 35726 | FALSE
Substation | Current Transformer | 240kV | 2000:1 | New | 59076 | each | facility | substation | L&M | 50% | 50% | 0% |  | 681306 | FALSE
Substation | Current Transformer | 138kV | 1200:1 | New | 37284 | each | facility | substation | L&M | 50% | 50% | 0% |  | 862432 | FALSE
Substation | Voltage Transformer | 240kV | 1050kV | New | 45937 | each | facility | substation | L&M | 50% | 50% | 0% |  | 87816 | FALSE
Substation | Voltage Transformer | 138kV | 650kV | New | 35726 | each | facility | substation | L&M | 50% | 50% | 0% |  | 1979015 | FALSE
Substation | Potential Transformer | 240kV | 1050kV | New | 45937 | each | facility | substation | L&M | 50% | 50% | 0% |  | 1838739 | FALSE
Substation | Potential Transformer | 138kV | 650kV | New | 35726 | each | facility | substation | L&M | 50% | 50% | 0% | unique size for all new stations, one for each new sub or if there is transformer added in existing sub | 44036 | FALSE
Substation | VAR Cap Bank | 240kV | xMVA | New | 681306 | each | facility | substation | L&M | 50% | 50% | 0% | 2 per CB; 1 per bus tie if applicable; 1 per line termination; 1 per transformer | 73617 | FALSE
Substation | VAR Cap Bank | 138kV | xMVA | New | 862432 | each | facility | substation | L&M | 50% | 50% | 0% | 2 per CB; 1 per bus tie if applicable; 1 per line termination; 1 per transformer | 51736 | FALSE
Substation | VAR Cap Bank | 25kV | xMVA | New | 87816 | each | facility | substation | L&M | 50% | 50% | 0% | 2 per feeder | 42812 | FALSE
Substation | VAR Reactor | 240kV | xMVA | New | 1979015 | each | facility | substation | L&M | 50% | 50% | 0% | 1 for each line end | 526092 | FALSE
Substation | VAR Reactor | 138kV | xMVA | New | 1838739 | each | facility | substation | L&M | 50% | 50% | 0% | 1 for each line end | 331983 | FALSE
Substation | Station Service | S.S transformer | 75kVA | New | 44036 | each | facility | substation | L&M | 50% | 50% | 0% | 1 main bus for each end of diameter; 1 extra main bus for each line termination | 21375 | FALSE
Substation | Air Break | 240kV | 1050kV | New | 73617 | each | facility | substation | L&M | 50% | 50% | 0% | 1 main bus for each end of diameter; 1 extra main bus for each line termination | 10687 | FALSE
Substation | Air Break | 138kV | 650kV | New | 51736 | each | facility | substation | L&M | 50% | 50% | 0% | for green site | 448546 | FALSE
Substation | Air Break | 25kV | 100kV | New | 42812 | each | facility | substation | L&M | 50% | 50% | 0% |  | 639780 | FALSE
Substation | Line Termination | 240kV | 1050kV | New | 526092 | each | facility | substation | L&M | 50% | 50% | 0% | new relay or module. 4 per new transformer; 3 per new line termination; 2 per bus; 2 per group of CB, e.g. 2 for 240kV and 2 for 138kV; | 50553 | FALSE
Substation | Line Termination | 138kV | 650kV | New | 331983 | each | facility | substation | L&M | 50% | 50% | 0% |  | 426520 | FALSE
Substation | Main Bus | 240kV | 4000A | New | 21375 | each | facility | substation | L&M | 50% | 50% | 0% | last item to be estimated, 3% x "SubTotal" in $K. E.g. if the SubTotal is $2,000,000, then 3% x 2000=60 | 1000 | FALSE
Substation | Main Bus | 138kV | 2000A | New | 10687 | each | facility | substation | L&M | 50% | 50% | 0% |  | 1348870 | FALSE
Substation | Control Building | 4mx14m | pre-fab | New | 448546 | each | facility | substation | L&M | 50% | 50% | 0% |  | 799725 | FALSE
Substation | Switchgear Building | 7-cell | pre-fab | New | 639780 | each | facility | substation | L&M | 50% | 50% | 0% |  | 433984 | FALSE
Substation | Protection & Control | relays/modules | pre-fab | New | 50553 | each | facility | substation | L&M | 50% | 50% | 0% |  | 1348870 | FALSE
Substation | Circuit Breaker | 500kV | 2000kV | New | 426520 | each | facility | substation | L&M | 50% | 50% | 0% |  | 799725 | FALSE
Substation | All sub commissioning | All sub commissioning | All sub commissioning | New | 1 | each | facility | substation | L&M | 0% | 100% | 0% |  | 433984 | FALSE
Line | 138kV | S/C | 1x477 | New (0~1km) | 1348870 | /km | facility | line | L&M | 50% | 50% | 0% |  | 1291933 | FALSE
Line | 138kV | S/C | 1x477 | New (1~10km) | 799725 | /km | facility | line | L&M | 50% | 50% | 0% |  | 765968 | FALSE
Line | 138kV | S/C | 1x477 | New (10+km) | 433984 | /km | facility | line | L&M | 50% | 50% | 0% |  | 415666 | FALSE
Line | 138kV | S/C | 2x477 | New (0~1km) | 1348870 | /km | facility | line | L&M | 50% | 50% | 0% |  |  | FALSE
Line | 138kV | S/C | 2x477 | New (1~10km) | 799725 | /km | facility | line | L&M | 50% | 50% | 0% |  | 1748732 | FALSE
Line | 138kV | S/C | 2x477 | New (10+km) | 433984 | /km | facility | line | L&M | 50% | 50% | 0% |  | 1041775 | FALSE
Line | 138kV | S/C | 1x266 | New (0~1km) | 1291933 | /km | facility | line | L&M | 50% | 50% | 0% |  |  | FALSE
Line | 138kV | S/C | 1x266 | New (1~10km) | 765968 | /km | facility | line | L&M | 50% | 50% | 0% |  | 2001445 | FALSE
Line | 138kV | S/C | 1x266 | New (10+km) | 415666 | /km | facility | line | L&M | 50% | 50% | 0% |  | 945808 | FALSE
Line | 138kV | D/C | 1x477 | New (0~1km) |  | /km | facility | line | L&M | 50% | 50% | 0% |  | 2384246 | FALSE
Line | 138kV | D/C | 1x477 | New (1~10km) | 1748732 | /km | facility | line | L&M | 50% | 50% | 0% |  | 1192123 | FALSE
Line | 138kV | D/C | 1x477 | New (10+km) | 1041775 | /km | facility | line | L&M | 50% | 50% | 0% |  | 951140 | FALSE
Line | 240kV | S/C | 2x477 | New (0~1km) |  | /km | facility | line | L&M | 50% | 50% | 0% |  |  | TRUE
Line | 240kV | S/C | 2x477 | New (1~10km) | 2001445 | /km | facility | line | L&M | 50% | 50% | 0% |  | 1167599 | FALSE
Line | 240kV | S/C | 2x477 | New (10+km) | 945808 | /km | facility | line | L&M | 50% | 50% | 0% |  |  | FALSE
Line | 240kV | S/C | 2(1)x795 | New (0~1km) | 2384246 | /km | facility | line | L&M | 50% | 50% | 0% |  |  | FALSE
Line | 240kV | S/C | 2(1)x795 | New (1~10km) | 1192123 | /km | facility | line | L&M | 50% | 50% | 0% |  |  | FALSE
Line | 240kV | S/C | 2(1)x795 | New (10+km) | 951140 | /km | facility | line | L&M | 50% | 50% | 0% |  | 1665561 | FALSE
Line | 240kV | D/C | 2x795 | New (0~1km) |  | /km | facility | line | L&M | 50% | 50% | 0% |  | 2439694 | FALSE
Line | 240kV | D/C | 2x795 | New (1~10km) | 1167599 | /km | facility | line | L&M | 50% | 50% | 0% |  |  | FALSE
Line | 240kV | D/C | 2x795 | New (10+km) |  | /km | facility | line | L&M | 50% | 50% | 0% |  | 58437 | FALSE
Line | 240kV | D/C single side strung | 2x795 | New (0~1km) |  | /km | facility | line | L&M | 50% | 50% | 0% |  | 29205 | FALSE
Line | 240kV | D/C single side strung | 2x795 | New (1~10km) |  | /km | facility | line | L&M | 50% | 50% | 0% |  | 121461 | FALSE
Line | 240kV | D/C single side strung | 2x795 | New (10+km) | 1665561 | /km | facility | line | L&M | 50% | 50% | 0% |  | 7.4% | FALSE
Line | 240kV | D/C | 2x1033 | New | 2439694 | /km | facility | line | L&M | 50% | 50% | 0% |  | 5.6% | FALSE
Line | 500kV | S/C | 2X1033 | New |  | /km | facility | line | L&M | 50% | 50% | 0% |  | 15.7% | FALSE
Telecom | Equipment | Equipment/Building |  | New | 58437 | Lot | facility | telecom | L&M | 50% | 50% | 0% |  | 3% | FALSE
Telecom | Fiber |  |  | New | 29205 | Lot | facility | telecom | L&M | 50% | 50% | 0% |  | 3% | FALSE
Telecom | Tower/Radio | Steel |  | New | 121461 | each | facility | telecom | L&M | 50% | 50% | 0% |  | 3% | FALSE
Distributed | Project Management | Project Management |  |  | 7.4% |  | non-facility | Disrtibuted | labour | 0% | 100% | 0% |  | 6.9% | FALSE
Distributed | Construction Management | Construction Management |  |  | 5.6% |  | non-facility | Disrtibuted | labour | 0% | 100% | 0% |  | 6.9% | FALSE
Distributed | Contingency | Contingency |  |  | 15.7% |  | non-facility | Disrtibuted |  | 0% | 0% | 100% |  |  | FALSE
Owners | Proposal to Provide Service | Proposal to Provide Service |  |  | 3% |  | non-facility | Owners | [6 empty] | FALSE
Owners | Facility Application | Facility Application |  |  | 3% |  | non-facility | Owners | [6 empty] | FALSE
Owners | Land related cost | Land related cost |  |  | 3% |  | non-facility | Owners | [6 empty] | FALSE
Other | AFUDC | AFUDC |  |  | 6.9% | [9 empty] | FALSE
Other | E&S | E&S |  |  | 6.9% | [9 empty] | FALSE